## Change Control
1_00 | 2020-03-13
First Release
|  | Enxxx | Code | Description
2_00 | 2020-03-20 | EN302 | 600-021 | Ambient Temperature & Humidity (EN302) TX T&H AMB 600-021
| Added Installation Packet to all worksheets | EN303 | 600-022 | Ambient T&H and VOC (EN303) TX VOC/T&H AMB 600-022
|  | EN304 | 600-023 | Ambient T&H/ VOC / CO2 (EN304) TX CO2/VOC/T&H AMB 600-023
2_01 | 2020-03-22 | EN305 | 600-031 | Tx Temp with Internal Temp Sensor (EN305) TX TEMP INS 600-031
| Changed worksheet names to match product code, not name | EN306 | 600-232 | Tx Temp PT1000 2-Ch (EN306) TX TEMP CONT2 600-232
|  | EN307 | 600-035 | Tx Analog 4-20mA (EN307) TX 4/20 mA 600-035
2_02 | 2020-03-24 | EN308 | 600-036 | Tx Pulse (EN308) TX PULSE 600-036
| Added new Product (EN324) - same as EN304 but without VOC | EN309 | 600-037 | Tx Pulse Atex (EN309) TX PULSE ATEX 600-037
| assuming type 14 for new product - to be confirmed after development | EN310 | 600-038 | Tx Pulse LED (EN310) TX PULSE LED 600-038
| also to confirm alarm setting during development | EN311 | 600-034 | Tx T&H with External Probe (EN311) TX T&H 600-034
|  | EN312 | 600-032 | Tx Temp PT1000 1-Ch (EN312) TX TEMP CONT1 600-032
3_00 | 2020-04-24 | EN313 | 600-033 | Tx Temp PT1000 1-Ch Ext Power (EN313) TX TEMP CONT1 MP 600-033
| Corrected Battery Level Status bits, added bit 0 for normal or alarm message | EN314 | 600-233 | Tx Temp PT1000 2-Ch Ext Power (EN314) TX TEMP CONT2 MP 600-233
|  | EN319 | 600-039 | Tx Contact (EN319) TX CONTACT 600-039
|  | EN324 | 600-024 | Ambient T&H / CO2 (EN324) TX CO2/T&H AMB 600-024
4_00 | 2020-11-27
Added Negative temperature calcualtion in temperature transmitters
5_00 | 2021-03-17
Added Negative temperature Setting calcualtion in temperature transmitters
6_00 | 2022-03-29
Error on displaying status of Pulse / Contact Inputs
Corrected all Pulse sheets EN308, EN309, EN310, EN319
7_00 | 31 May 2022
Removed useless sheets 600-024, 600-033 and 600-233
Corrected TWU setting to Fixed
7_01 | 08 July 2022
Corrected Retries setting to Fixed

## 600-021
Enter LoRaWAN String Below for Analysis
00006D041301FFE501200000000000080000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 00006D | 109 | Transmitter ID
7 | 2 | 04 | 4 | 4 = Ambient T&H Sensor
9 | 2 | 13 | 19 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | FFE5 | -2.7 | Temperature
17 | 4 | 0120 | 28.8 | Humidity
21 | 4 | 0000 | 0 | VOC
25 | 4 | 0000 | 0 | CO2
29 | 4 | 0008 | 8 | Alarm Status | 00000000 | 00001000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hum Lo Alm | Hum Hi OK | Temp Lo OK | Temp Hi OK
33 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000019000C8032001900000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Hi Temp Alarm (degC) |  | 40 | 0190
P2 |  |  | Lo Temp Alarm (degC) |  | 20 | 00C8
P3 |  |  | Hi Hum Alarm (%) |  | 80 | 0320
P4 |  |  | Lo Hum Alarm (%) |  | 40 | 0190
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-022
Enter LoRaWAN String Below for Analysis
00007705110100E3011F0014000000280000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 000077 | 119 | Transmitter ID
7 | 2 | 05 | 5 | 5 = Ambient T&H / VOC Sensor
9 | 2 | 11 | 17 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | 00E3 | 22.7 | Temperature
17 | 4 | 011F | 28.7 | Humidity
21 | 4 | 0014 | 20 | VOC
25 | 4 | 0000 | 0 | CO2
29 | 4 | 0028 | 40 | Alarm Status | 00000000 | 00101000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOC Lo Alm | VOC Hi OK | Hum Lo Alm | Hum Hi OK | Temp Lo OK | Temp Hi OK
33 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000015E00C80320019002BC012C00000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Hi Temp Alarm (degC) |  | 35 | 015E
P2 |  |  | Lo Temp Alarm (degC) |  | 20 | 00C8
P3 |  |  | Hi Hum Alarm (%) |  | 80 | 0320
P4 |  |  | Lo Hum Alarm (%) |  | 40 | 0190
P5 |  |  | VOC Hi Alarm (ppb) |  | 700 | 02BC
P6 |  |  | VOC Lo Alarm (ppb) |  | 300 | 012C
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-023
Enter LoRaWAN String Below for Analysis
000081060E1100D3016500AD026100800000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 000081 | 129 | Transmitter ID
7 | 2 | 06 | 6 | 6 = Ambient T&H / VOC / CO2 Sensor
9 | 2 | 0E | 14 | Sequential Counter
11 | 2 | 11 | 00010001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | 00D3 | 21.1 | Temperature
17 | 4 | 0165 | 35.7 | Humidity
21 | 4 | 00AD | 173 | VOC
25 | 4 | 0261 | 609 | CO2
29 | 4 | 0080 | 128 | Alarm Status | 00000000 | 10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CO2 Lo Alm | CO2 Hi OK | VOC Lo OK | VOC Hi OK | Hum Lo OK | Hum Hi OK | Temp Lo OK | Temp Hi OK
33 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000012C009601F400C800C80032028A00FA000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Hi Temp Alarm (degC) |  | 30 | 012C
P2 |  |  | Lo Temp Alarm (degC) |  | 15 | 0096
P3 |  |  | Hi Hum Alarm (%) |  | 50 | 01F4
P4 |  |  | Lo Hum Alarm (%) |  | 20 | 00C8
P5 |  |  | VOC Hi Alarm (ppb) |  | 200 | 00C8
P6 |  |  | VOC Lo Alarm (ppb) |  | 50 | 0032
P7 |  |  | CO2 Hi Alarm (ppm) |  | 650 | 028A
P8 |  |  | CO2 Lo Alarm (ppm) |  | 250 | 00FA
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-031
Enter LoRaWAN String Below for Analysis
00008A07070100CD000000020000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 00008A | 138 | Transmitter ID
7 | 2 | 07 | 7 | 7 = Temp Ins
9 | 2 | 07 | 7 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | 00CD | 20.5 | Temperature
17 | 4 | 0000 | 0 | Temperature 2
21 | 4 | 0002 | 2 | Alarm Status | 00000000 | 00000010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Temp Lo Alm | Temp Hi OK
25 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000015E00C8000000000000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Hi Temp Alarm (degC) |  | 35 | 015E
P2 |  |  | Lo Temp Alarm (degC) |  | 20 | 00C8
P3 |  |  | Fixed (0) |  | 0 | 0000
P4 |  |  | Fixed (0) |  | 0 | 0000
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-232
Enter LoRaWAN String Below for Analysis
0000BD0C0A0100CE00CA00010000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 0000BD | 189 | Transmitter ID
7 | 2 | 0C | 12 | 12 = Tx Temp Cont2
9 | 2 | 0A | 10 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | 00CE | 20.6 | Temperature
17 | 4 | 00CA | 20.2 | Temperature 2
21 | 4 | 0001 | 1 | Alarm Status | 00000000 | 00000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Temp2 Lo OK | Temp2 Hi OK | Temp1 Lo OK | Temp1 Hi Alm
25 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000015E00C8032001900000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Hi Temp Ch1 Alarm (degC) |  | 35 | 015E
P2 |  |  | Lo Temp Ch1 Alarm (degC) |  | 20 | 00C8
P3 |  |  | Hi Temp Ch2 Alarm (degC) |  | 80 | 0320
P4 |  |  | Lo Temp Ch2 Alarm (degC) |  | 40 | 0190
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-035
Enter LoRaWAN String Below for Analysis
0000C70D0A01000200020000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 0000C7 | 199 | Transmitter ID
7 | 2 | 0D | 13 | 13= 4-20mA Tx
9 | 2 | 0A | 10 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | 0002 | 0.002 | 4-20mA Value
17 | 4 | 0002 | 2 | Alarm Status | 00000000 | 00000010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4-20 Lo Alm | 4-20 Hi OK
21 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000067201C201F400000000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | 4-20 Hi Alarm |  | 16.5 | 0672
P2 |  |  | 4-20 Lo Alarm |  | 4.5 | 01C2
P3 |  |  | Loop Power (msecs) |  | 500 | 01F4
P4 |  |  | Fixed (0) |  | 0 | 0000
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-036
Enter LoRaWAN String Below for Analysis
000095080C0100000020000000170000001E00000000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 000095 | 149 | Transmitter ID
7 | 2 | 08 | 8 | 8 = Tx Pulse
9 | 2 | 0C | 12 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 8 | 00000020 | 32 | Pulse Ch1
21 | 8 | 00000017 | 23 | Pulse Ch2
29 | 8 | 0000001E | 30 | Pulse OC
37 | 4 | 0000 | 0 | Alarm Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | OC Leak OK | Ch2 Leak OK | Ch1 Leak OK | 0 | OC Lo Flow OK | Ch2 Lo Flow OK | Ch1 Lo Flow OK | 0 | OC Hi Flow OK | Ch2 Hi Flow OK | Ch1 Hi Flow OK
41 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OC Open | Ch2 Open | Ch1 Open | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C000000000064000A0001000F00C8001400020019012C001E0003002301
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Input 1 Flow Hi |  | 100 | 0064
P2 |  |  | Input 1 Flow Lo |  | 10 | 000A
P3 |  |  | Input 1 Flow Time (Hrs) |  | 1 | 0001
P4 |  |  | Input 1 Leak Threshold |  | 15 | 000F
P5 |  |  | Input 2 Flow Hi |  | 200 | 00C8
P6 |  |  | Input 2 Flow Lo |  | 20 | 0014
P7 |  |  | Input 2 Flow Time (Hrs) |  | 2 | 0002
P8 |  |  | Input 2 Leak Threshold |  | 25 | 0019
P9 |  |  | OC Flow Hi |  | 300 | 012C
P10 |  |  | OC Flow Lo |  | 30 | 001E
P11 |  |  | OC Flow Time (Hrs) |  | 3 | 0003
P12 |  |  | OC Leak Threshold |  | 35 | 0023
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-037
Enter LoRaWAN String Below for Analysis
0000A0090D01000000120000001A0000001800000000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 0000A0 | 160 | Transmitter ID
7 | 2 | 09 | 9 | 9 = Tx Pulse Atex
9 | 2 | 0D | 13 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 8 | 00000012 | 18 | Pulse Ch1
21 | 8 | 0000001A | 26 | Pulse Ch2
29 | 8 | 00000018 | 24 | Pulse OC
37 | 4 | 0000 | 0 | Alarm Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | OC Leak OK | Ch2 Leak OK | Ch1 Leak OK | 0 | OC Lo Flow OK | Ch2 Lo Flow OK | Ch1 Lo Flow OK | 0 | OC Hi Flow OK | Ch2 Hi Flow OK | Ch1 Hi Flow OK
41 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OC Open | Ch2 Open | Ch1 Open | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C000000000064000A0001000F00C8001400020019012C001E0003002301
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Input 1 Flow Hi |  | 100 | 0064
P2 |  |  | Input 1 Flow Lo |  | 10 | 000A
P3 |  |  | Input 1 Flow Time (Hrs) |  | 1 | 0001
P4 |  |  | Input 1 Leak Threshold |  | 15 | 000F
P5 |  |  | Input 2 Flow Hi |  | 200 | 00C8
P6 |  |  | Input 2 Flow Lo |  | 20 | 0014
P7 |  |  | Input 2 Flow Time (Hrs) |  | 2 | 0002
P8 |  |  | Input 2 Leak Threshold |  | 25 | 0019
P9 |  |  | OC Flow Hi |  | 300 | 012C
P10 |  |  | OC Flow Lo |  | 30 | 001E
P11 |  |  | OC Flow Time (Hrs) |  | 3 | 0003
P12 |  |  | OC Leak Threshold |  | 35 | 0023
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-038
Enter LoRaWAN String Below for Analysis
0000AA0A0D0100000000000000000000000A00000060
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 0000AA | 170 | Transmitter ID
7 | 2 | 0A | 10 | 10 = Tx Pulse LED
9 | 2 | 0D | 13 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 8 | 00000000 | 0 | Pulse Ch1
21 | 8 | 00000000 | 0 | Pulse Ch2
29 | 8 | 0000000A | 10 | Pulse OC
37 | 4 | 0000 | 0 | Alarm Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | OC Leak OK | Ch2 Leak OK | Ch1 Leak OK | 0 | OC Lo Flow OK | Ch2 Lo Flow OK | Ch1 Lo Flow OK | 0 | OC Hi Flow OK | Ch2 Hi Flow OK | Ch1 Hi Flow OK
41 | 4 | 0060 | 96 | Status | 00000000 | 01100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OC Open | Ch2 Closed | Ch1 Closed | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C0000000000000000000000000000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Fixed (0) |  | 0 | 0000
P2 |  |  | Fixed (0) |  | 0 | 0000
P3 |  |  | Fixed (0) |  | 0 | 0000
P4 |  |  | Fixed (0) |  | 0 | 0000
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-034
Enter LoRaWAN String Below for Analysis
0000D10E0A0100CA018200010000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 0000D1 | 209 | Transmitter ID
7 | 2 | 0E | 14 | 14 = Tx T&H
9 | 2 | 0A | 10 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | 00CA | 20.2 | Temperature
17 | 4 | 0182 | 38.6 | Humidity
21 | 4 | 0001 | 1 | Alarm Status | 00000000 | 00000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hum Lo OK | Hum Hi OK | Temp Lo OK | Temp Hi Alm
25 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000015E00C8032001900000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Hi Temp Alarm (degC) |  | 35 | 015E
P2 |  |  | Lo Temp Alarm (degC) |  | 20 | 00C8
P3 |  |  | Hi Hum Alarm (%) |  | 80 | 0320
P4 |  |  | Lo Hum Alarm (%) |  | 40 | 0190
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-032
Enter LoRaWAN String Below for Analysis
0000DC0F0A0100D0000000000000
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 0000DC | 220 | Transmitter ID
7 | 2 | 0F | 15 | 15 = TxTemp Cont1
9 | 2 | 0A | 10 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 4 | 00D0 | 20.8 | Temperature
17 | 4 | 0000 | 0 | Temperature 2
21 | 4 | 0000 | 0 | Alarm Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Temp Lo OK | Temp Hi OK
25 | 4 | 0000 | 0 | Status | 00000000 | 00000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Normal
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C00000000015E00C8000000000000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Hi Temp Alarm (degC) |  | 35 | 015E
P2 |  |  | Lo Temp Alarm (degC) |  | 20 | 00C8
P3 |  |  | Fixed (0) |  | 0 | 0000
P4 |  |  | Fixed (0) |  | 0 | 0000
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01

## 600-039
Enter LoRaWAN String Below for Analysis
0000B40B0E0100000018000000280000005600040001
Start | Count | HEX VALUE | DEC / BIN
1 | 6 | 0000B4 | 180 | Transmitter ID
7 | 2 | 0B | 11 | 11 = Tx Contact
9 | 2 | 0E | 14 | Sequential Counter
11 | 2 | 01 | 00000001 | F/W (bits 3-0), Settings (bits 7-4)
13 | 8 | 00000018 | 24 | Pulse Ch1
21 | 8 | 00000028 | 40 | Pulse Ch2
29 | 8 | 00000056 | 86 | Pulse OC
37 | 4 | 0004 | 4 | Alarm Status | 00000000 | 00000100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OC No Change Alm | Ch2 No Change OK | Ch1 No Change OK
41 | 4 | 0001 | 1 | Status | 00000000 | 00000001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | OC Open | Ch2 Open | Ch1 Open | 0 | 0 | 0 | 0 | Alarm
Bits 3-2 for battery level Battery Level 00 for 100% 01 for 75% 10 for 50% 11 for 25%
Below is used to construct the message to re-configure transmitter via the LoRaWAN network
Generic Field Names |  |  | Transmitter Specific Fields (only change those in Green) |  |  | Hex | Copy String Below and use to send on LoRaWAN network
Fixed |  |  | Fixed (0) |  | 0 | 000000 | 000000030000012C000000000005000A000000000000000000000000000000000000000001
Installation Packet = 3 |  |  | Fixed (3) |  | 3 | 03
Fixed |  |  | Fixed (0) |  | 0 | 0000
RE-Tx Time (secs) |  |  | Periodicity (mins) |  | 5 | 012C
Fixed |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (0) |  | 0 | 0000
P1 |  |  | Input 1 delay before Tx (secs) |  | 5 | 0005
P2 |  |  | Input 2 delay before Tx (secs) |  | 10 | 000A
P3 |  |  | Fixed (0) |  | 0 | 0000
P4 |  |  | Fixed (0) |  | 0 | 0000
P5 |  |  | Fixed (0) |  | 0 | 0000
P6 |  |  | Fixed (0) |  | 0 | 0000
P7 |  |  | Fixed (0) |  | 0 | 0000
P8 |  |  | Fixed (0) |  | 0 | 0000
P9 |  |  | Fixed (0) |  | 0 | 0000
P10 |  |  | Fixed (0) |  | 0 | 0000
P11 |  |  | Fixed (0) |  | 0 | 0000
P12 |  |  | Fixed (0) |  | 0 | 0000
Fixed |  |  | Fixed (1) |  | 1 | 01